## ram345
generator1 willow
|  | Incremental MW | initial(0) | 5 | 10 | 15 | 20 | 25
Line |  | MW Output changed | 10 | 15 | 20 | 25 | 30 | 35
from | to
Ram138 | homer138 | MW | 569.7563 | 568.5001 | 567.2491 | 565.9983 | 564.7478 | 563.4975
|  | experimental sensitivity | 15: -0.25123
|  | Sensitivity from simulator | -0.25028 | -0.25023 | -0.25018 | -0.25013 | -0.25009 | -0.25004
Ram138 | monarch138 | MW | 664.1399 | 663.0279 | 661.9191 | 660.8105 | 659.7021 | 658.5939
experimental sensitivity
|  | Sensitivity from simulator | -0.22182 | -0.22178 | -0.22174 | -0.2217 | -0.22166 | -0.22162
Ram138 | willow138 | MW | 556.2128 | 554.88 | 553.551 | 552.2222 | 550.8936 | 549.5653
experimental sensitivity
|  | Sensitivity from simulator | -0.26588 | -0.26683 | -0.26578 | -0.26573 | -0.26568 | -0.26564
generator2 lion
|  | Incremental MW | initial(0) | 5 | 10 | 15 | 20 | 25
Line |  | MW Output changed | 35 | 40 | 45 | 50 | 55 | 60
from | to
Ram138 | homer138 | MW | 569.7563 | 569.4875 | 569.2239 | 568.9604 | 568.697 | 568.4336
experimental sensitivity
|  | Sensitivity from simulator | -0.052745 | -0.052728 | -0.052711 | -0.052695 | -0.052678 | -0.052661
Ram138 | monarch138 | MW | 664.1399 | 663.8623 | 663.588 | 663.3138 | 663.0396 | 662.7655
experimental sensitivity
|  | Sensitivity from simulator | -0.054882 | -0.054868 | -0.054854 | -0.054841 | -0.054827 | -0.054813
Ram138 | willow138 | MW | 556.2128 | 555.9575 | 555.706 | 555.4546 | 555.2032 | 554.952
|  | experimental sensitivity | 40: -0.05106
|  | Sensitivity from simulator | -0.050327 | -0.05031 | -0.050293 | -0.050276 | -0.050259 | -0.050242

## phase shifter
line/transformer flow sensitivities(0-->+30-->-30)
| monarch138 |  | willow138 |  | holmer138 |  |  | monarch138 |  | willow138 |  | holmer138
shifter degree | MW | sensitivity | MW | sensitivity | MW | sensitivity | shifter degree | MW | sensitivity | MW | sensitivity | MW | sensitivity
0 | 664.1361 |  | 556.2084 |  | 569.7506 |  | 0 | 664.1366 |  | 556.2089 |  | 569.7511
2 | 671.7365 |  | 560.3682 |  | 573.5207 |  | -2 | 656.6219 |  | 552.1836 |  | 566.1108
4 | 679.4008 |  | 564.656 |  | 577.4148 |  | -4 | 649.2055 |  | 548.2974 |  | 562.6046
6 | 687.1405 |  | 569.0672 |  | 581.4287 |  | -6 | 641.9004 |  | 544.5559 |  | 559.2374
8 | 694.9187 |  | 573.5964 |  | 585.5578 |  | -8 | 634.7197 |  | 540.9644 |  | 556.0139
10 | 702.7304 |  | 578.3386 |  | 589.7973 |  | -10 | 627.6763 |  | 537.5284 |  | 552.9392
12 | 710.5629 |  | 582.9884 |  | 594.1425 |  | -12 | 620.7834 |  | 534.2535 |  | 550.0182
14 | 718.4033 |  | 587.8407 |  | 598.589 |  | -14 | 614.054 |  | 531.1453 |  | 547.256
16 | 726.2389 |  | 592.7905 |  | 603.132 |  | -16 | 607.5014 |  | 528.2095 |  | 544.6578
18 | 734.0568 |  | 597.8326 |  | 607.767 |  | -18 | 601.1388 |  | 525.452 |  | 542.2289
20 | 741.8446 |  | 602.9621 |  | 612.4897 |  | -20 | 594.9795 |  | 522.8788 |  | 539.9748
22 | 749.5896 |  | 608.174 |  | 617.2954 |  | -22 | 589.0371 |  | 520.4963 |  | 537.9011
24 | 757.2792 |  | 613.4634 |  | 622.18 |  | -24 | 583.3253 |  | 518.3108 |  | 536.0138
26 | 764.9011 |  | 618.8256 |  | 627.1392 |  | -26 | 577.8582 |  | 516.3294 |  | 534.319
28 | 772.4429 |  | 624.2559 |  | 632.1688 |  | -28 | 572.6092 |  | 514.5195 |  | 532.7849
30 | 779.8923 |  | 629.75 |  | 637.2651 |  | -30 | 567.6407 |  | 512.9358 |  | 531.4641

## LTC
Tap setting | 0.9 | 0.9125 | 0.925 | 0.9375 | 0.095 | 0.9625 | 0.975 | 0.9875 | 1 | 1.0125 | 1.025 | 1.375 | 1.05 | 1.0625 | 1.075 | 1.0875 | 1.1
Total losses(MW) | 289.77 | 289.55 | 289.39 | 289.28 | 289.21 | 289.19 | 289.22 | 289.28 | 289.38 | 289.52 | 289.69 | 289.88 | 290.19 | 290.49 | 290.82 | 291.17 | 291.53

## capacitors bank
bus no | bus name | initial losses | after losses |  | order to switch on
30 | Bear138 | 289.28 | 283.09 | 6.19 | 3
28 | peach138 |  | 283.72 | 5.56 | 5
24 | rose138 |  | 280.06 | 9.22 | 1
29 | illini138 |  | 280.8 | 8.48 | 2
3 | hawk345 |  | 286.92 | 2.36 | 6
40 | lion345 |  | 289.11 | 0.17 | never choose
39 | willow138 |  | 289.28 | 0
8 | apple345 |  | 283.71 | 5.57 | 4
close one capacitor
bus no | bus name | initial losses | after losses
8 | apple345 | 283.71 | closed
30 | Bear138 |  | 279.42
28 | peach138 |  | 279.96
24 | rose138 |  | 276.5
29 | illini138 |  | 277.24
3 | hawk345 |  | 282.3
40 | lion345 |  | 283.67
39 | willow138 |  | 283.71
LTC | initial position | losses | optimal position | losses
HAWK | 0.9625 | 263.49 | 0.9625 | 261.57
badger | 0.9625 |  | 0.9
bear | 0.9625 |  | 0.9
tiger | 0.9625 |  | 0.9

## P-V ash138
P (Mw) | Voltage(kv) | degree
210 | 110.8522 | -17.76
220 | 110.0657 | -18.37
230 | 109.2333 | -19.01
240 | 108.348 | -19.68
250 | 107.4014 | -20.38
260 | 106.382 | -21.12
270 | 105.2744 | -21.92
280 | 104.0568 | -22.78
|  |  | Bus Name | Skip | Processed | Solved | Violation
|  |  | Valley138 | No | Yes | No | Unsolved
|  |  | Peach138 | No | Yes | No | Unsolved
|  |  | Rose138 | No | Yes | No | Unsolved
|  |  | Apple345 | No | Yes | No | Unsolved
|  |  | Illini345 | No | Yes | No | Unsolved
|  |  | Tiger138 | No | Yes | No | Unsolved
|  |  | Bear138 | No | Yes | No | Unsolved
|  |  | Bear345 | No | Yes | No | Unsolved
|  |  | Ram345 | No | Yes | No | Unsolved
|  |  | Viking345 | No | Yes | No | Unsolved
|  |  | Illini138 | No | Yes | No | Unsolved
|  |  | Bus Name | Skip | Processed | Solved | Violation
|  |  | Apple345 | No | Yes | No | Unsolved
|  |  | Viking345 | No | Yes | No | Unsolved
|  |  | Bus Name | Skip | Processed | Solved | Violation
|  |  | Valley138 | No | Yes | Yes | Unsolved
|  |  | Peach138 | No | Yes | Yes | Unsolved
|  |  | Rose138 | No | Yes | Yes | Unsolved
|  |  | Apple345 | No | Yes | Yes | Unsolved
|  |  | Illini345 | No | Yes | Yes | Unsolved
|  |  | Tiger138 | No | Yes | Yes | Unsolved
|  |  | Bear138 | No | Yes | Yes | Unsolved
|  |  | Bear345 | No | Yes | Yes | Unsolved
|  |  | Ram345 | No | Yes | Yes | Unsolved
|  |  | Viking345 | No | Yes | Yes | Unsolved
|  |  | Illini138 | No | Yes | Yes | Unsolved